## APP A.1 - Non-Driven
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | Comms Channel | Comms Controller | Comms Address | Equipment ID | Service | Device Type | MCC No | Rated Power (kW) | Rated (KVA) | Full Load (Amps) | Duty | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
Not Identified

## APP A.2 - Driven Equipment
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | State 0 Text | State 1 Text | State 1 Input | Command Output DO[1] | Command Output DO[2] | Power | ESD | Local/Remote | Duty/Stanby | Start Time | Stop Time | Maintenance Statistics | Prog Start | Prog Stop | Permissive Start | Permissive Bypass | I/lock Stop | I/lock Bypass | Safety I/lock | Alarm Priority | Alarm Disable | P&ID | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
A30P002 | Elec - NA Lube Oil Pump(30P002) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P002_K1 | A30P002_K3 | NA | No | No | No | No | 5s | 5s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0070 | C&I Sheet:1C & 7 | Arunkumar | 2021-09-13
A30KEH1 | Elec - NA Comp Oil Htr (30KEH1) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | OFF | ON | A30KEH1_K1 | A30KEH1_K3 | NA | No | No | No | No | 5s | 5s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0070 | C&I Sheet:1C & 7 | Arunkumar | 2021-09-13
A30P014 | Elec - Drip Acid Pump (30P014) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P014_K1 | A30P014_K3 | NA | No | No | No | No | 5s | 5s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0020 | C&I Sheet:1F & 13 | Arunkumar | 2021-09-13
A30P021 | Elec - Waste Water Pump (30P021) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P021_K1 | A30P021_K3 | NA | No | No | No | No | 15s | 15s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0020 | C&I Sheet:1F & 14 | Arunkumar | 2021-09-13
A30P008A | Elec - Acid Condy Pump (30P008A) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P008A_K1 | A30P008A_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0029 | C&I Sheet:1A & 3 | Arunkumar | 2021-09-13
A30P008B | Elec - Acid Condy Pump (30P008B) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P008B_K1 | A30P008B_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0029 | C&I Sheet:1A & 3 | Arunkumar | 2021-09-13
A30K003 | Elec - Lube Oil Mist Fan (30K003) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30K003_K1 | A30K003_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0070 | C&I Sheet:1C & 7 | Arunkumar | 2021-09-13
A30P012A | Elec - BFW Pump 30P012A | Q_PWR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P012A_K1 | A30P012A_K3 | NA | EA_99021 | No | No | Yes | 60s | 60s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0046 | C&I Sheet:1G & 15 | Arunkumar | 2021-10-29
A30P012B | Elec - BFW Pump 30P012B | Q_PWR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P012B_K1 | A30P012B_K3 | NA | EA_99021 | No | No | Yes | 60s | 60s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0046 | C&I Sheet:1G & 16 | Arunkumar | 2021-10-29
A30P005A | Elec -Emergency BFW Pump 30P005A | Q_PWR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P005A_K1 | A30P005A_K3 | NA | EA_99045 | No | No | Yes | 60s | 60s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0046 | C&I Sheet:1G & 17 | Arunkumar | 2021-10-29
A30P005B | Elec -Emergency BFW Pump 30P005B | Q_PWR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P005B_K1 | A30P005B_K3 | NA | EA_99045 | No | No | Yes | 60s | 60s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0046 | C&I Sheet:1G & 18 | Arunkumar | 2021-10-29
A30P009A | Elec - NA Stm Condy Pmp (30P009A) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P009A_K1 | A30P009A_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0030 | C&I Sheet:1H & 20 | Arunkumar | 2021-10-29
A30P009B | Elec - NA Stm Condy Pmp (30P009B) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P009B_K1 | A30P009B_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0030 | C&I Sheet:1H & 20 | Arunkumar | 2021-10-29
A38P001A | Elec - NA Storage Pump (38P001A) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA38 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A38P001A_K1 | A38P001A_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | High |  | QN-VT-38-D-0005 | C&I Sheet:1J & 23 | Arunkumar | 2021-10-29
A38P001B | Elec - NA Storage Pump (38P001B) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA38 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A38P001B_K1 | A38P001B_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | High |  | QN-VT-38-D-0005 | C&I Sheet:1J & 23 | Arunkumar | 2021-10-29
A30P004A | Elec-Sec Air Condensate (30P004A) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | EA_30330A | HS_30334B | NA | No | No | No | No | 5s | 5s | No | [7 empty] | Urgent |  | QN-VT-30-D-0090 | C&I Sheet:1K & 25 | Arunkumar | 2021-10-29
A30P004B | Elec-Sec Air Condensate (30P004B) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | EA_30331A | HS_30336B | NA | No | No | No | No | 5s | 5s | No | [7 empty] | Urgent |  | QN-VT-30-D-0090 | C&I Sheet:1K & 25 | Arunkumar | 2021-10-29
A30K001 | Elec - NA Compressor (30K001) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30K001_Q005 | A30K001_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0012 | C&I Sheet:1L & 36 | Arunkumar | 2021-10-29
A30P007A | Elec - Acid Condy Pump (30P007A) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P007A_K1 | A30P007A_K3 | NA | No | No | No | Yes | 10s | 10s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0022 | C&I Sheet:37 | Arunkumar | 2021-10-29
A30P007B | Elec - Acid Condy Pump (30P007B) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30P007B_K1 | A30P007B_K3 | NA | No | No | No | Yes | 10s | 10s | Yes | [7 empty] | Urgent |  | QN-VT-30-D-0022 | C&I Sheet:37 | Arunkumar | 2021-10-29
A30P010B | Elec - 2ndyAir LO Aux Pump-30P010B | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | EA_30337 | HS_30333B | NA | No | No | No | No | 5s | 5s | No | [7 empty] | Urgent |  | QN-VT-30-D-0080 | C&I Sheet:38 | Arunkumar | 2021-10-29
A30K005A | Elec - | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | A30K005_K1 | A30K005_K3 | NA | No | No | No | No | 10s | 10s | Yes | [7 empty] | Low |  |  | C&I Sheet:Equipment | Arunkumar | 2021-10-29
A30K005 | Elec - Sec Air Fltr Blwr (30K005) | Q_MTR211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | STOP | START | ES_30348 | HS_30348 | NA | No | No | No | No | 20s | 10s | No | [7 empty] | Urgent |  | QN-VT-30-D-0013 | C&I Sheet:Equipment | Arunkumar | 2021-10-29
AT_30067_CUPT | RunTime - AT30067 Stack Analyser | DEVCTLA | Device Control For cumulative time | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | IDLE | RUNNING | NA | NA | NA | NA | NA | NA | NA | NA | NA | Yes | [7 empty] | None |  | QN-VT-30-D-0010 | C&I Sheet:46 | Arunkumar | 2021-10-29

## APP A.3 - Selectors
PCS Tagname | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | Type | No of States | State 0 Desc | State 1 Desc | State 2 Desc | State 3 Desc | State 4 Desc | State 5 Desc | State 6 Desc | State 7 Desc | Alarm Priority | P&ID | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
HS_30P012 | A30P012A/B - Duty/Standby Selector | DEVCTLA | DEVCTLA Selector | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Latched | 2 | A30P012B_DUTY | A30P012A_DUTY | [7 empty] | QN-VT-30-D-0046 | C&I Sheet: 15 | Arunkumar T M | 2021-10-29
HS_30P005 | A30P005A/B - Duty/Standby Selector | DEVCTLA | DEVCTLA Selector | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Latched | 2 | A30P005B_DUTY | A30P005A_DUTY | [7 empty] | QN-VT-30-D-0046 | C&I Sheet: 17 | Arunkumar T M | 2021-10-29
HS_30P007 | A30P007A/B - Duty/Standby Selector | DEVCTLA | DEVCTLA Selector | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Latched | 2 | A30P007B_DUTY | A30P007A_DUTY | [7 empty] | QN-VT-30-D-0022 | C&I Sheet: 37 | Arunkumar T M | 2021-10-29
HSA_30387B | Logic - NA MP Steam Vent | Q_DISHSA | FLAGA | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Latched | 2 | NONE | OVERRIDE | [6 empty] | Low | QN-VT-30-D-0032 | C&I Sheet: 22 | Arunkumar T M | 2021-10-29
HS_30328 | 30K010 Load | Q_DISHSA | FLAGA | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Latched | 2 | NONE | LOAD | [8 empty] | C&I Sheet: Simple PID Logic | Arunkumar T M | 2021-10-29
HS_30152 | NH3 Start | Q_DISHSA | FLAGA with Pulse | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Pulsed | 2 | NONE | START | [8 empty] | C&ID sheet: SIS Logic | Arunkumar T M | 2021-10-29
AT_30067_SS | NOx Stack Analyser HMI Service Switch | Q_DISHSA | FLAGA | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Latched | 2 | NONE | SERVICE | [8 empty] | C&ID sheet: 42-47 | Arunkumar T M | 2021-10-29
HS_30074 | Secondary Air to Primary Reset | Q_DISHSA | FLAGA with Pulse | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Pulsed | 2 | NONE | RESET | [7 empty] | QN-VT-30-D-0011 | C&ID sheet: 49 | Arunkumar T M | 2021-10-29
AT_30056_SS | NOx Analyser HMI Service Switch | Q_DISHSA | FLAGA | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Latched | 2 | NONE | SERVICE | [7 empty] | QN-VT-30-D-0100 | C&ID sheet: 50 | Arunkumar T M | 2021-10-29
HS_30511 | Reset NOx Trip | Q_DISHSA | FLAGA with Pulse | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Pulsed | 2 | NONE | RESET | [7 empty] | QN-VT-30-D-0100 | C&ID sheet: 50 | Arunkumar T M | 2021-10-29
HS_30133 | pH NA CWT return Calibration Switch | Q_DISHSA | FLAGA | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Latched | 2 | NONE | CALIB | [8 empty] | C&ID sheet: 51 | Arunkumar T M | 2021-10-29
HS_30322A_CMD | Run up to Minimum speed | Q_DISHSA | FLAGA with Pulse | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Pulsed | 2 | NONE | START | [7 empty] | QN-VT-30-D-0013 | C&ID sheet: 53 | Arunkumar T M | 2021-10-29
HS_30322B_CMD | Run to Rated speed | Q_DISHSA | FLAGA with Pulse | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Pulsed | 2 | NONE | RAMP_UP | [7 empty] | QN-VT-30-D-0013 | C&ID sheet: 53 | Arunkumar T M | 2021-10-29
HS_30322C_CMD | Run down to Minimum speed | Q_DISHSA | FLAGA with Pulse | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Pulsed | 2 | NONE | RAMP_DOWN | [7 empty] | QN-VT-30-D-0013 | C&ID sheet: 53 | Arunkumar T M | 2021-10-29
HS_30322D_CMD | 30K010 Stop | Q_DISHSA | FLAGA with Pulse | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Pulsed | 2 | NONE | STOP | [7 empty] | QN-VT-30-D-0013 | C&ID sheet: 53 | Arunkumar T M | 2021-10-29
Note on A5: V, Vidya Sneha: Source assumed to be HMI

## APP A.5 - Digital Controllers
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | State 0 Text | State 1 Text | State 0 Input | State 1 Input | State 0 Time | State 1 Time | Permissive Open | Permissive Close | Permissive Bypass | Auto Open | Auto Close | I/lock Open | I/lock Close | I/lock Bypass | Safety I/lock | Alarm Priority | OP Destination Tag | Bad PV Priority | Alarm Disable | P&ID | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
XN_30140 | Air to 30MT02 | DEVCTLA | Device Control with 2 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | CLOSE | OPEN | ZSL_30140_DCS | ZSH_30140_DCS | 60s | 60s |  |  |  | C&I Sheet: 9 | C&I Sheet: 9 |  |  |  |  | Urgent | XV_30140 |  |  | QN-VT-30-D-0070 | C&I Sheet: 1D & 9 | Arunkumar | 2021-09-13
XV_30297 | Inst. Air to 30MT02 | Q_BV211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | CLOSE | OPEN | -XN_30297 | XN_30297 | 10s | 10s |  |  |  | C&I Sheet: 10 | C&I Sheet: 10 |  | C&I Sheet: 10 |  |  | Urgent | XN_30297 |  |  | QN-VT-30-D-0065 | C&I Sheet: 1D & 9 | Arunkumar | 2021-09-13
XV_30288 | Nitric Acid ex 30C001 | Q_BV211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | CLOSE | OPEN | ZSL_30288 | -ZSL_30288 | 10s | 10s |  |  |  | C&I Sheet: 12 | C&I Sheet: 12 |  |  |  |  | Urgent | XN_30288 |  |  | QN-VT-30-D-0027 | C&I Sheet:1E & 12 | Arunkumar | 2021-09-13
XV_30280 | Seal Gas 30MT02 | Q_BV211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | OPEN | CLOSE | -XN_30280 | XN_30280 | 10s | 10s |  |  |  | C&I Sheet: 27 | C&I Sheet: 27 |  |  |  |  | Urgent | XN_30280 |  |  | QN-VT-30-D-0065 | C&I Sheet: 1D & 27 | Arunkumar | 2021-10-29
XN_30056A | NOx Stream 1 | Q_BV211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | OPEN | CLOSE | -XV_30056A | XV_30056A | 10s | 10s |  |  |  | C&I Sheet: 27 | C&I Sheet: 27 |  |  |  |  | Urgent | XV_30056A |  |  |  | C&I Sheet: 27 | Arunkumar | 2021-10-29
XN_30056B | NOx Stream 1 | Q_BV211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | CLOSE | OPEN | -XV_30056B | XV_30056B | 10s | 10s |  |  |  | C&I Sheet: 27 | C&I Sheet: 27 |  |  |  |  | Urgent | XV_30056B |  |  |  | C&I Sheet: 27 | Arunkumar | 2021-10-29
XV_30052 | NH3 to 30R003 | Q_BV211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | OPEN | CLOSE | XN_30052 | -XN_30052 | 10s | 10s |  |  |  | C&I Sheet: 28 | C&I Sheet: 28 |  |  |  |  | Urgent | XN_30052 |  |  | QN-VT-30-D-0015 | C&I Sheet: 1O & 28 | Arunkumar | 2021-10-29
XV_30053 | NH3 Vent | Q_BV211 | Device Control with 1 DI & 1 DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | CLOSE | OPEN | XN_30053 | -XN_30053 | 10s | 10s |  |  |  | C&I Sheet: 28 | C&I Sheet: 28 |  |  |  |  | Urgent | XN_30053 |  |  | QN-VT-30-D-0015 | C&I Sheet: 1O & 28 | Arunkumar | 2021-10-29

## APP A.4 - Digital Status
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | Direction | HW DI Tag | HW DO Tag | State 0 Desc | State 1 Desc | Normal State | Delay Time | Off Normal Priority | Bad PV Priority | Alarm Disable | P&ID | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
ZAL_30006 | Pos - PV30006 NH3 ex 30E001 Open | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30006 |  | N_OPENED | OPENED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0005 | C&I Sheet: 6 | Arunkumar | 2021-09-13
UA_30002 | Run time-Drip Acid Pmp (30P014) | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  | N/A |  | NORMAL | ALARM | State0 |  | Urgent | (HOLD) |  | QN-VT-30-D-0070 | C&I Sheet: 7 | Arunkumar | 2021-09-13
TAHH_30276 | Temp - Lube Oil Sump (30K001) HiHi | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | TSHH_30276 |  | ALARM | NORMAL | State1 |  | None | NONE |  | QN-VT-30-D-0070 | C&I Sheet: 8 | Arunkumar | 2021-09-13
ZAL_30090 | Nitric Acid ex 30C001 | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30090 |  | N_CLOSED | CLOSED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 11 | Arunkumar | 2021-09-13
LAL_30088 | Level - Abs.Tower (30C001) Lo | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | LSL_30088 |  | ALARM | NORMAL | State1 |  | Urgent | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 12 | Arunkumar | 2021-09-13
LAL_30089 | Level - Abs.Tower (30C001) Lo | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | LISL_30089 |  | ALARM | NORMAL | State1 |  | Low | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 12 | Arunkumar | 2021-09-13
ZAL_30288 | Nitric Acid ex 30C001 | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30288 |  | N_CLOSED | CLOSED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 12 | Arunkumar | 2021-09-13
TA_30P014 | Run time-Drip Acid Pmp (30P014) | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0020 | C&I Sheet: 13 | Arunkumar | 2021-09-13
LAH_30099 | Level - Drip Acid Pit Hi | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | LSH_30099 |  | ALARM | NORMAL | State1 | ON - 10m | Low | (HOLD) |  | QN-VT-30-D-0020 | C&I Sheet: 14 | Arunkumar | 2021-10-29
LAL_30099 | Level - Drip Acid Pit Lo | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | LSL_30099 |  | ALARM | NORMAL | State1 |  | (HOLD) | (HOLD) |  | QN-VT-30-D-0020 | C&I Sheet: 14 | Arunkumar | 2021-09-13
I_30_52_DCS | Low BFW Circulation Flow | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | I_30_52 |  | NORMAL | LOW | State0 |  | None | NONE |  |  | C&I Sheet: 19 | Arunkumar | 2021-10-29
A30P012A_ALM | Elec - BFW Pump 30P012A Alarm | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | NONE |  | QN-VT-30-D-0046 | C&I Sheet: 15 | Arunkumar | 2021-10-29
A30P012B_ALM | Elec - BFW Pump 30P012B Alarm | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | NONE |  | QN-VT-30-D-0046 | C&I Sheet: 16 | Arunkumar | 2021-10-29
A30P005A_ALM | Elec -Emergency BFW Pump 30P005A Alarm | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | NONE |  | QN-VT-30-D-0046 | C&I Sheet: 17 | Arunkumar | 2021-10-29
A30P005B_ALM | Elec -Emergency BFW Pump 30P005B Alarm | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | NONE |  | QN-VT-30-D-0046 | C&I Sheet: 18 | Arunkumar | 2021-10-29
EA_30419 | 30P012A Motor Unavailable | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | A30P012A_K5 |  | ALARM | NORMAL | State1 |  | Urgent | (HOLD) |  | QN-VT-30-D-0046 |  | Arunkumar | 2021-10-29
EA_30423 | 30P012B Motor Unavailable | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | A30P012B_K5 |  | ALARM | NORMAL | State1 |  | Urgent | (HOLD) |  | QN-VT-30-D-0046 |  | Arunkumar | 2021-10-29
EA_30415 | 30P005A Motor Unavailable | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | A30P005A_K5 |  | ALARM | NORMAL | State1 |  | Urgent | (HOLD) |  | QN-VT-30-D-0046 |  | Arunkumar | 2021-10-29
EA_30434 | 30P005B Motor Unavailable | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | A30P005B_K5 |  | ALARM | NORMAL | State1 |  | Urgent | (HOLD) |  | QN-VT-30-D-0046 |  | Arunkumar | 2021-10-29
EA_30484 | 30P012A/B Auto Operation Disable | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | (HOLD) |  | QN-VT-30-D-0046 | C&I Sheet: 19 | Arunkumar | 2021-10-29
XA_30480 | 30P005A/B Auto Operation Disable | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | (HOLD) |  | QN-VT-30-D-0046 | C&I Sheet: 19 | Arunkumar | 2021-10-29
XA_30387A | PIC_30087A Intrlkd to MAN 100% | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | High | (HOLD) |  | QN-VT-30-D-0032 | C&I Sheet: 21 | Arunkumar | 2021-10-29
XA_30387B | PIC_30087B Intrlkd to MAN | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | High | (HOLD) |  | QN-VT-30-D-0032 | C&I Sheet: 21 | Arunkumar | 2021-10-29
EA_30327 | Status - SAC Common Trip 30K010 | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | XS_30327 |  | NORMAL | TRIP | State0 |  | Urgent | (HOLD) |  | QN-VT-30-D-0013 | C&I Sheet: 22 | Arunkumar | 2021-10-29
EA99021D | AN Plant Load-Shed Trip | Q_DISALM | Soft Alarm | AREA99 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | LOADSHED | State0 |  | Urgent | (HOLD) |  |  | In Progress - To be developed | Arunkumar | 2021-10-29
LALL_30361 | Status - 30P004A/B Low Lvl Trip | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | High | (HOLD) |  | QN-VT-30-D-0090 | C&I Sheet: 25 | Arunkumar | 2021-10-29
EA_30330B_STS | Cond. Pump A30P004A Status | Q_DISALM | HW DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct |  | EA_30330B | STOPPED | RUNNING | None |  | None | (HOLD) |  | QN-VT-30-D-0090 | C&I Sheet: 25 | Arunkumar | 2021-10-29
EA_30331B_STS | Cond. Pump A30P004A Status | Q_DISALM | HW DO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct |  | EA_30331B | STOPPED | RUNNING | None |  | None | (HOLD) |  | QN-VT-30-D-0090 | C&I Sheet: 25 | Arunkumar | 2021-10-29
EA_30339_FAIL | Status - 30P004A/B Duty Fail | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | EA_30339 |  | NORMAL | ALARM | State0 |  | Urgent | (HOLD) |  | QN-VT-30-D-0090 |  | Arunkumar | 2021-10-29
HS_30017Q_SEL | HMI Selector FT30017/FT30021 via PLC-NA Ratio | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | HS_30017Q |  | FT30021 | FT30017 | None |  | None | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
ZAL_30017 | Posn - FV30017 NH3/AIR to mixer | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30017 |  | N_CLOSED | CLOSED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0020 |  | Arunkumar | 2021-10-29
XA_30068 | TIC_30068 Interlocked to MAN 0% | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | High | (HOLD) |  | QN-VT-30-D-0021 | C&I Sheet: 28 | Arunkumar | 2021-10-29
UA_30511 | AI_30056 - NOx Trip Degraded | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | (HOLD) |  |  | C&I Sheet: 27 | Arunkumar | 2021-10-29
ZAL_30052 | Posn - XV30051 NH3 to 30R003 | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30052 |  | N_CLOSED | CLOSED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0015 |  | Arunkumar | 2021-10-29
ZAH_30053 | Posn-XV30053 NH3 to 30R003 Bleed | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSH_30053 |  | N_OPENED | OPENED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0015 |  | Arunkumar | 2021-10-29
FAL_30133 | Flow - AI_30133 Sample Lo | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | FISL_30133 |  | NORMAL | ALARM | State0 | ON - 20s | Low | (HOLD) |  | QN-VT-30-D-0036 |  | Arunkumar | 2021-10-29
TAH_30251 | Temp - 30K001 Motor Hi | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | TISH_30251 |  | NORMAL | ALARM | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
LAH_30252 | 30K001 Mtr Water Level Hi | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | LSH_30252 |  | ALARM | NORMAL | State1 |  | Low | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
LAH_30294 | Level - Separator 30E030 Hi | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | LSH_30294 |  | ALARM | NORMAL | State1 |  | Low | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
LAH_30169 | Level - 30K001 Water Trap Hi | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | LSH_30169 |  | ALARM | NORMAL | State1 |  | Low | (HOLD) |  |  |  | Arunkumar | 2021-10-29
ZAL_30135 | Posn - XV30135 NH3 to 30E001 | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30135 |  | N_CLOSED | CLOSED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0005 |  | Arunkumar | 2021-10-29
FAL_30145 | Flow - Cond Conductivity Lo | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | FISL_30145 |  | NORMAL | ALARM | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0030 |  | Arunkumar | 2021-10-29
AA_30056SS | AT_30056 Service Switch On | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | High | (HOLD) |  | QN-VT-30-D-0100 |  | Arunkumar | 2021-10-29
ZAL_30051 | Posn - FV30051 NH3 gas to 30R003 | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30051 |  | N_CLOSED | CLOSED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0015 |  | Arunkumar | 2021-10-29
ZA_30051 | Fault - 30R003 NH3 Seq Fault | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | High | (HOLD) |  |  |  | Arunkumar | 2021-10-29
EA_30329 | Status - SAC Common Alarm 30K010 | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | EA_30329 |  | NORMAL | ALARM | State0 |  | High | (HOLD) |  | QN-VT-30-D-0013 |  | Arunkumar | 2021-10-29
XA_30390 | LIC_30390 Interlocked to MAN 0% | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0032 | C&I Sheet: PID_Interlock Logic | Arunkumar | 2021-10-29
ZAH_30024 | Position -IGV Error -FIC in MAN | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 | ON - 2s 500ms | Urgent | (HOLD) |  | QN-VT-30-D-0012 | C&I Sheet: 32 | Arunkumar | 2021-10-29
A30K001_FLT | Elec - NA Compressor (30K001) Fault | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | A30K001_K5 |  | FAULT | NORMAL | None |  | NONE | NONE |  | QN-VT-30-D-0012 | C&I Sheet: 36 | Arunkumar | 2021-10-29
ZSLL_30025_STS | PV30025A - Fully Closed | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSLL_30025 |  | N_CLOSED | CLOSED | None |  | NONE | NONE |  | QN-VT-30-D-0012 | C&I Sheet: 39 | Arunkumar | 2021-10-29
ZSLL_30025B_STS | PV30025B - Fully Closed | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSLL_30025B |  | N_CLOSED | CLOSED | None |  | NONE | NONE |  | QN-VT-30-D-0012 | C&I Sheet: 39 | Arunkumar | 2021-10-29
ZALL_30025 | Pos - 30K001 Discharge Vlvs FC | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | (HOLD) |  | QN-VT-30-D-0012 | C&I Sheet: 39 | Arunkumar | 2021-10-29
XA_30426 | PIC_30426 Interlocked to MAN 0% | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | ALARM | NORMAL | State1 |  | Low | (HOLD) |  | QN-VT-30-D-0032 | C&I Sheet: 40 | Arunkumar | 2021-10-29
ZAL_30019 | Posn- XV_30019 NH3 Feed | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30019 |  | N_CLOSED | CLOSED | State0 | ON - 20s | Low | (HOLD) |  |  |  | Arunkumar | 2021-10-29
ZAH_30020 | Posn - XV_30020 NH3/Air Bleed | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSH_30020 |  | N_OPENED | OPENED | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
XA_30384 | TIC_30384 Interlocked to MAN 50% | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 | ON - 20s | High | (HOLD) |  | QN-VT-30-D-0032 | C&I Sheet: 41 | Arunkumar | 2021-10-29
XA_30067_FLT | Device Fault - AT30067 Analyser | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | XA_30067 |  | FAULT | NORMAL | State1 |  | Urgent | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
XA_30067A_FLT | Comms Fault - AT30067 Analyser | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | XA_30067A |  | FAULT | NORMAL | State1 |  | Urgent | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
AA_30067SS | AT_30067 Service Switch On | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | High | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
AQA_30067FG | Conc - AVG NOx approach DEHP Lim | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Urgent | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
ZAH_30058 | Pos- XV30058 TG turbine bypass | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSH_30058 |  | N_OPENED | OPENED | State0 |  | Low | (HOLD) |  |  |  | Arunkumar | 2021-10-29
ZAL_30058 | Pos - XV30058 TG turb byps Close | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30058 |  | N_CLOSED | CLOSED | State0 |  | Low | (HOLD) |  |  |  | Arunkumar | 2021-10-29
XA_30319_FLT | Fault - FT30319 Stack Meter | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | XA_30319 |  | FAULT | NORMAL | State1 |  | Urgent | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
AT_30067FG_BQUAL | AT_30067FG Bad Quality | FLAGA | FLAGA | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | BAD | None |  | NONE | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 46 | Arunkumar | 2021-10-29
UA_30133SS | Service Switch - NA CW Return pH | Q_DISALM | Soft Alarm | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 |  |  |  | NORMAL | ALARM | State0 |  | Low | (HOLD) |  |  | C&I Sheet: 51 | Arunkumar | 2021-10-29
PDAH_30270 | DP - Oil Filters (30F001A/B) Hi | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | PDS_30270 |  | ALARM | NORMAL | State1 |  | Low | (HOLD) |  |  |  | Arunkumar | 2021-10-29
ZAL_30082 | Secondary Air to 30C001 | Q_DISALM | HW DI | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | Direct | ZSL_30082 |  | NORMAL | ALARM | State0 |  | Low | (HOLD) |  | QN-VT-30-D-0021 | C&I Sheet:30 | Arunkumar | 2021-10-29
Note on A3: V, Vidya Sneha: "_" added
Note on P9: V, Vidya Sneha: Self-Acknowledge functionality

## APP A.6 - Analogue Indicators
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | EU Range Low | EU Range High | Eng Units | PV Ext Range Low | PV Ext Range High | PV Format | PV Char | Low cutoff | Filter Time | Input Direction | PV Source | PV Clamping | PV High High Value | PV High High DB | PV High High Priority | PV High Value | PV High DB | PV High Priority | PV Low Value | PV Low DB | PV Low Priority | PV Low Low Value | PV Low Low DB | PV Low Low Priority | ROC Pos Value | ROC Pos Priority | ROC Neg Value | ROC Neg Priority | Bad PV Priority | Alarm Disable | P&ID | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
ZI_30002 | Valve LV_30002 position | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  |  | LIC_30002.PIDA.OP | NoClamp | 100 | 0.5 | Urgent | 95 | 0.5 | High | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0005 | C&I Sheet: 5 | Arunkumar | 2021-09-13
PI_30005 | Press - 30E001 NH3 Evaporator | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 4000 | kPa | -116 | 4116 | D0 | Linear |  |  | Direct | PT_30005 | NoClamp | 2000 | 0.5 | High | 1400 | 0.5 | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0005 | C&I Sheet: 6 | Arunkumar | 2021-09-13
PI_30272 | Press - Lube oil 30K001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 250 | kPag | -7.25 | 257.25 | D1 | Linear |  |  | Direct | PT_30272 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | 180 | 0.5 | Low | 160 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0070 | C&I Sheet: 7 | Arunkumar | 2021-09-13
TI_30275 | Temp - Lube Oil Sump (30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | DegC | -2.9 | 102.9 | D2 | Linear |  |  | Direct | TT_30275 | NoClamp | 80 | 0.5 | Urgent | 40 | 0.5 | NONE | 30 | 0.5 | NONE | 25 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0070 | C&I Sheet: 8 | Arunkumar | 2021-09-13
LI_30273 | Level - 30K001 Oil Sump | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | LT_30273 | NoClamp | 100 | 0.5 | Urgent | 100 | 0.5 | Low | 66 | 0.5 | Low | 66 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0070 | C&I Sheet: 8 | Arunkumar | 2021-09-13
PI_30064 | Press - TG turbine inlet | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | kPag | -58 | 2058 | D0 | Linear |  |  | Direct | PT_30064 | NoClamp | 2000 | 0.5 | Urgent | 850 | 0.5 | Low | 730 | 0.5 | Low | 250 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 | C&I Sheet: 9 | Arunkumar | 2021-09-13
LI_30097 | Level - Drip Acid 30D014 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | LT_30097 | NoClamp | 90 | 5 | Urgent | 84.3 | 0.5 | NONE | 45 | 0.5 | NONE | 30 | 5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0020 | C&I Sheet: 13 | Arunkumar | 2021-09-13
FI_30317 | Flow - MP Steam to 30MT01 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 12000 | kg/h | -348 | 12348 | D0 | Linear |  |  | Direct | FT_30317 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0085 | C&I Sheet: 22 | Arunkumar | 2021-10-29
LI_38001 | Level - NA Tank 38T001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA38 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | LT_38001 | NoClamp | 98 | 7 | Urgent | 90 | 1 | High | 15 | 1 | Low | 8 | 7 | Low |  |  |  |  | (HOLD) |  | QN-VT-38-D-0005 | C&I Sheet: 23 | Arunkumar | 2021-10-29
LI_38015 | Level - NA Tank 38T002 | Q_ANALM | HW Analogue Indicator With Alarming | AREA38 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | LT_38015 | NoClamp | 98 | 8 | Urgent | 90 | 1 | High | 15 | 1 | Low | 8 | 7 | Low |  |  |  |  | (HOLD) |  | QN-VT-38-D-0010 | C&I Sheet: 23 | Arunkumar | 2021-10-29
FTY_30017_L | Flow Uncomp - NH3/Air to Mixer | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 7500 | kg/hr | -217.5 | 7717.5 | D0 | Square Root | 525 |  | Direct | FT_30017 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 26 | Arunkumar | 2021-10-29
FI_30017 | Flow - NH3/Air to Mixer | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 7500 | kg/hr | -217.5 | 7717.5 | D0 | Linear |  |  |  | FTY_30017.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 26 | Arunkumar | 2021-10-29
PI_30014 | Press - NH3/Air to Mixer | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | kPag | -58 | 2058 | D0 | Linear |  |  | Direct | PT_30014 | NoClamp | 1950 | 0.5 | Urgent | 1300 | 0.5 | Low | 800 | 0.5 | Low | 100 | 0.5 | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 26 | Arunkumar | 2021-10-29
TI_30013 | Temp - NH3/Air to Mixer | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | DegC | -4.35 | 154.35 | D1 | Linear |  |  | Direct | TT_30013 | NoClamp | 150 | 0.5 | Urgent | 120 | 0.5 | Low | 77 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 26 | Arunkumar | 2021-10-29
FTY_30037_L | Flow Uncomp - Primary Air ex 30K001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 120000 | kg/hr | -3480 | 123480 | D0 | Square Root | 8400 |  | Direct | FT_30017 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0011 | C&I Sheet: 26 | Arunkumar | 2021-10-29
FI_30037 | Flow - Primary Air ex 30K001 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 120000 | kg/hr | -3480 | 123480 | D0 | Linear |  |  |  | FTY_30037.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | 43000 | 0.5 | Low | 35000 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0011 | C&I Sheet: 26 | Arunkumar | 2021-10-29
PI_30033 | Press - Prim Air Flow ex 30K001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | kPag | -58 | 2058 | D0 | Linear |  |  | Direct | PT_30033 | NoClamp | 2000 | 1 | Urgent | 980 | 1 | High | 450 | 1 | Low | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0011 | C&I Sheet: 26 | Arunkumar | 2021-10-29
TI_30032 | Temp - Prim Air Flow ex 30K001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 300 | DegC | -8.7 | 308.7 | D1 | Linear |  |  | Direct | TT_30032 | NoClamp | NONE | NONE | NONE | 260 | 0.5 | High | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0011 | C&I Sheet: 26 | Arunkumar | 2021-10-29
FI_30021 | Flow (Coriolis) - NH3 to Mixer | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 7500 | kg/h | -217.5 | 7717.5 | D0 | Linear |  |  | Direct | FT_30021 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 26 | Arunkumar | 2021-10-29
FFI_30017 | NH3/AIR to mixer | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 5 | 15 | %Ratio | 4.71 | 15.29 | D3 | Linear |  |  |  |  | NoClamp | 10.8 | 0.05/ON - 2s | Urgent | 10.6 | 0.05/ON - 2s | Low | 9.5 | 0.05/ON - 5s | NONE | 9 | 0.05/ON - 5s | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 26 | Arunkumar | 2021-10-29
PI_30281 | Press - Seal Gas (30MT02) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 600 | kPag | -17.4 | 617.4 | D1 | Linear |  |  | Direct | PT_30281 | NoClamp | 600 | 0.5 | Urgent | 250 | 5 | NONE | 240 | 15 | Low | 15 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0065 | C&I Sheet: 27 | Arunkumar | 2021-10-29
FTY_30080_L | Flow Uncomp - Sec. Air to 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 21000 | kg/hr | -609 | 21609 | D0 | Square Root | 1470 | 0.08 | Direct | FT_30080 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0021 | C&I Sheet: 30 | Arunkumar | 2021-10-29
FI_30080 | Sec. Air to 30C001 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 21000 | kg/hr | -609 | 21609 | D0 | Linear |  |  |  | FTY_30080.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | 7000 | 100 | High | 5000 | 100/ ON - 10s | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0021 | C&I Sheet: 30 | Arunkumar | 2021-10-29
TI_30081 | Temp - Sec. Air to 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | DegC | -4.35 | 154.35 | D1 | Linear |  |  | Direct | TT_30081 | NoClamp | 150 | 0.5 | Urgent | 120 | 0.5 | Low | 50 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0021 | C&I Sheet: 30 | Arunkumar | 2021-10-29
TI_30054 | Temp - TG to SCR | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 100 | 400 | DegC | 91.3 | 408.7 | D1 | Linear |  |  | Direct | TT_30054 | NoClamp | 400 | 0.5 | Urgent | 360 | 0.5 | Low | 250 | 0.5 | Low | 190 | 0.5 | Urgent |  |  |  |  | (HOLD) |  |  | C&I Sheet: 27 | Arunkumar | 2021-10-29
AT_30056AVG | Conc(NOx) -TailGas | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | ppm | -58 | 2058 | D0 | Linear |  |  |  | AI_30056.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0100 | C&I Sheet: Moving Average | Arunkumar | 2021-10-29
FT_30091AVG | Flow - Acid Mass Flow ex 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 50000 | m3/h | -1450 | 51450 | D0 | Linear |  |  |  | FI_30091.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0027 | C&I Sheet: Moving Average | Arunkumar | 2021-10-29
FTY_30017AVG | Avg Flow - Sec. Air to 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 7500 | kg/hr | -217.5 | 7717.5 | D0 | Linear |  |  |  | FFY_30017.SELREALA.OUT | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: Moving Average | Arunkumar | 2021-10-29
FT_30051AVG | Avg Flow - NH3 gas to 30R003 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 60 | kg/hr | -1.74 | 61.74 | D2 | Linear |  |  |  | FIC_30051.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0015 | C&I Sheet: Moving Average | Arunkumar | 2021-10-29
FI_30222 | Flow - CW to 2ry Air Comp 30K010 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 900 | t/h | -26.1 | 926.1 | D1 | Linear |  |  | Direct | FT_30222 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0013 |  | Arunkumar | 2021-10-29
PI_30152 | Press - 2ry Air Discharge 30K010 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1400 | kPa | -40.6 | 1440.6 | D0 | Linear |  |  | Direct | PT_30152 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0013 |  | Arunkumar | 2021-10-29
SI_30132 | Speed - 2ry Air Comp 30K010 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 4200 | rpm | -121.8 | 4321.8 | D0 | Linear |  |  | Direct | ST_30132 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  |  |  | Arunkumar | 2021-10-29
AI_30091 | Dens - Acid ex AbsCol (30C001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | kg/m3 | -58 | 2058 | D0 | Linear |  |  | Direct | AT_30091 | NoClamp | 1500 | 0.5 | Urgent | 1350 | 0.5 | Low | 1200 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 31 | Arunkumar | 2021-10-29
AI_30091A | Conc(NA) - NA ex AbsCol (30C001) | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  |  |  | NoClamp | NONE | NONE | NONE | 61 | 0.2 | Low | 57 | 0.2 | Low | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 31 | Arunkumar | 2021-10-29
FI_30091 | Flow - Acid Mass Flow ex 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 50000 | kg/hr | -1450 | 51450 | D0 | Linear |  |  | Direct | FT_30091 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 31 | Arunkumar | 2021-10-29
FI_30091A | Flow - Acid Vol Flow ex 30C001 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 40 | m3/hr | -1.16 | 41.16 | D2 | Linear |  |  |  |  | NoClamp | NONE | NONE | NONE | 35 | 1 | High | 12 | 0.5 | Low | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 31 | Arunkumar | 2021-10-29
TI_30091 | Temp - Acid ex 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | DegC | -2.9 | 102.9 | D2 | Linear |  |  | Direct | TT_30091 | NoClamp | 100 | 0.5 | Urgent | 65 | 0.5 | Low | 30 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet: 31 | Arunkumar | 2021-10-29
AI_30091A_L | Conc(NA) - NA ex AbsCol (30C001) | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  | 1 |  | AI_30091A.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0027 | C&I Sheet: 31 | Arunkumar | 2021-10-29
FQ_30091 | Totalized Flow - Acid Mass Flow ex 30C001 | TOTALIZER | Totalizer with PVAlgo | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 99999 | kg | -2899.971 | 102898.971 | D0 | Linear |  |  |  | FI_30091.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0027 | C&I Sheet: 31 | Arunkumar | 2021-10-29
ZI_30024 | PRV 30K001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 78 | -20 | Degree | 80.842 | -22.842 | D3 | Linear |  |  | Direct | ZT_30024 | NoClamp | 80 | 0.5 | Urgent | 70 | 0.5 | Low | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
PY_3022 | Press - TG to Expander (30MT02) | DACA | DACA with LeadLag | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | kPag | -58 | 2058 | D0 | Linear |  |  | Direct | PT_30225 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0012 | C&I Sheet: Simple_PID Logic | Arunkumar | 2021-10-29
TI_30379 | Temp - NA Catalyst Gauze 30R012 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1100 | DegC | -31.9 | 1131.9 | D0 | Linear |  |  |  | TY_30379.SELREALD.OUT | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0016 | C&I Sheet: 35 | Arunkumar | 2021-10-29
TI_30379A | Temp - NA Catalyst Gauze 30R012 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1100 | DegC | -31.9 | 1131.9 | D0 | Linear |  |  | Direct | TT_30379A | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 | C&I Sheet: 35 | Arunkumar | 2021-10-29
TI_30379B | Temp - NA Catalyst Gauze 30R012 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1100 | DegC | -31.9 | 1131.9 | D0 | Linear |  |  | Direct | TT_30379B | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 | C&I Sheet: 35 | Arunkumar | 2021-10-29
TI_30379C | Temp - NA Catalyst Gauze 30R012 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1100 | DegC | -31.9 | 1131.9 | D0 | Linear |  |  | Direct | TT_30379C | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 | C&I Sheet: 35 | Arunkumar | 2021-10-29
ZI_30143 | Posn - HV30143 Turbine IGV | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | -16 | 8 | Degree | -16.696 | 8.696 | D2 | Linear |  |  | Direct | ZT_30143 | NoClamp | 9.9 | 0.05 | Urgent | 9.9 | 0.05 | Low | -15 | 0.05 | Low | -15 | 0.05 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
II_30249 | Amps - 30K001 Motor | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 550 | Amps | -15.95 | 565.95 | D1 | Linear |  |  | Direct | IT_30249 | NoClamp | 500 | 10 | Urgent | 475 | 10 | Low | 0 | 10 | Low | 0 | 10 | Urgent |  |  |  |  | (HOLD) |  |  | C&I Sheet: 36 | Arunkumar | 2021-10-29
FI_30077 | Flow - NA to cooler condenser | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 10000 | kg/hr | -290 | 10290 | D0 | Linear |  |  | Direct | FT_30077 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | 5000 | 0.5 | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0022 | C&I Sheet: SIS Logic | Arunkumar | 2021-10-29
TI_30110 | Temp - BFW to 30E006 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 100 | 200 | DegC | 97.1 | 202.9 | D2 | Linear |  |  | Direct | TT_30110 | NoClamp | 200 | 0.5 | Urgent | 160 | 0.5 | Low | 130 | 0.5 | Low | 100 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0021 |  | Arunkumar | 2021-10-29
AI_30067A | Conc - NO from NA Plant | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 300 | ppm | -8.7 | 308.7 | D1 | Linear |  |  | Direct | AT_30067A | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 43 | Arunkumar | 2021-10-29
AI_30067A_B | Conc - NO from NA Plant | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | None |  |  |  |  | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 45 | Arunkumar | 2021-10-29
AI_30067B | Conc - NO from NA Plant | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | Linear |  |  | Direct | AT_30067B | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 43 | Arunkumar | 2021-10-29
AI_30067C | Conc - NO2 from NA Plant | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 300 | uS | -8.7 | 308.7 | D1 | Linear |  |  | Direct | AT_30067C | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 43 | Arunkumar | 2021-10-29
AI_30067C_D | Conc - NO2 from NA Plant | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | None |  |  |  |  | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 45 | Arunkumar | 2021-10-29
AI_30067D | Conc - NO2 from NA Plant | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | Linear |  |  | Direct | AT_30067D | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 43 | Arunkumar | 2021-10-29
AI_30067E | AT_30067E - N2O from NA Plant | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | Linear |  |  | Direct | AT_30067E | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 44 | Arunkumar | 2021-10-29
AI_30067E_H | AT_30067H - N2O from NA Plant | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | None |  |  |  |  | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 45 | Arunkumar | 2021-10-29
AI_30067F | Conc(NOx) -TailGas to Stack | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 300 | ppm | -8.7 | 308.7 | D1 | Linear |  | 5 | Direct | AT_30067F | NoClamp | 240 | 12 | High | 150 | 7.5 | Low | 0 | 0 | Low | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 44 | Arunkumar | 2021-10-29
AI_30067F_G | Conc - NOx from NA Plant | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | None |  |  |  |  | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | 25 | 0/ON-5m | Low | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 45 | Arunkumar | 2021-10-29
AI_30067G | Conc - NOx from NA Plant | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | Linear |  |  | Direct | AT_30067G | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 44 | Arunkumar | 2021-10-29
AI_30067H | AT_30067H - N2O from NA Plant | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | Linear |  |  | Direct | AT_30067H | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 | C&I Sheet: 44 | Arunkumar | 2021-10-29
AQI_30067FG | Conc - AVG NOX in NA Tailgas | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | ppm | -43.5 | 1543.5 | D0 | Linear |  |  |  |  | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
FQ_30051 | Totalized Flow - NH3 gas to 30R003 | TOTALIZER | Totalizer with PVAlgo | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 99999 | kg | -2899.971 | 102898.971 | D0 | Linear |  |  |  | FIC_30051.DACA.PV | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0015 | C&I Sheet: 31 | Arunkumar | 2021-10-29
PDI_30171 | DP - Secondary:Primary Air | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | -50 | 50 | kPa | -52.9 | 52.9 | D2 | Linear |  | 0.03 | Direct | PDT_30171 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | 5 | 3/ ON-5 | Low | -15 | 3/ ON-5 | High |  |  |  |  | (HOLD) |  | QN-VT-30-D-0011 |  | Arunkumar | 2021-10-29
AI_30056 | Conc(NOx) -TailGas | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | ppm | -58 | 2058 | D0 | None |  | 5 | Direct | AT_30056 | NoClamp | 240 | 12 | High | 150 | 7.5 | Low | 0 | 0 | Low | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0100 | C&I Sheet: 50 | Arunkumar | 2021-10-29
AI_30133 | pH - CW Return from Nitric Acid | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 10 | pH | -0.29 | 10.29 | D3 | Linear |  |  | Direct | AT_30133 | NoClamp | 9 | 0.2/ON - 1m | Urgent | 8.7 | 0.2/ON - 1m | Urgent | NONE | NONE | NONE | 7.5 | 0.5/ON - 1m | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0036 | C&I Sheet: 51 | Arunkumar | 2021-10-29
FI_30319 | Velocity - Stack | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 48 | m/sec | -1.392 | 49.392 | D2 | Linear |  |  | Direct | FT_30319 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 52 | Arunkumar | 2021-10-29
TI_30319 | Temp - Stack | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 80 | 120 | kPaa | 78.84 | 121.16 | D2 | Linear |  |  | Direct | TT_30319 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 52 | Arunkumar | 2021-10-29
PI_30319 | Press - Stack | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 600 | DegC | -17.4 | 617.4 | D1 | Linear |  |  | Direct | PT_30319 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 52 | Arunkumar | 2021-10-29
PDI_30001 | DP - NH3 filter 30F003A | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 60 | kPa | -1.74 | 61.74 | D2 | Linear |  | 5 | Direct | PDT_30001 | NoClamp | 50 | 0.5 | Low | 40 | 0.5 | Low | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0006 |  | Arunkumar | 2021-10-29
GI_30711 | Conc - NH3 at Drip Acid Pit | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | ppm | -2.9 | 102.9 | D2 | Linear |  |  | Direct | GD_30711 | NoClamp | 50 | 5 | Urgent | 25 | 5 | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  |  |  | Arunkumar | 2021-10-29
AI_30435 | Conc - NH3 at NA Reactor | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | ppm | -2.9 | 102.9 | D2 | Linear |  |  | Direct | AT_30435 | NoClamp | 50 | 25/ON - 10s | Critical | 25 | 5/ON - 10s | Critical | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 |  | Arunkumar | 2021-10-29
AI_30436 | Conc - NOx at NA Reactor | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 10 | ppm | -0.29 | 10.29 | D3 | Linear |  |  | Direct | AT_30436 | NoClamp | 5 | 1.5/ON - 10s | Critical | 3.5 | 1/ON - 10s | Critical | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 |  | Arunkumar | 2021-10-29
AI_30437 | Conc - NOx at NA Ground Floor | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 10 | ppm | -0.29 | 10.29 | D3 | Linear |  |  | Direct | AT_30437 | NoClamp | 5 | 1.5/ ON - 10s/ OFF - 5m | Critical | 3.5 | 1/ ON - 10s/ OFF - 5m | Critical | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 |  | Arunkumar | 2021-10-29
FY_30063 | Flow - 30K001 Total Air Flow | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 120000 | kg/hr | -3480 | 123480 | D0 | None |  |  |  |  | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  |  |  | Arunkumar | 2021-10-29
TI_30407 | Temp - NA Plant KO Pot | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | -33 | 100 | DegC | -36.857 | 103.857 | D1 | Linear |  |  | Direct | TT_30407 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | -15 | 0.5 | Urgent | NONE | NONE | NONE |  |  |  |  | NONE |  |  |  | Arunkumar | 2021-10-29
TI_30382 | Temp - NA Reactor 30R012 Exit | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 600 | DegC | -17.4 | 617.4 | D1 | Linear |  |  | Direct | TT_30382 | NoClamp | 440 | 5 | Urgent | 415 | 0/ ON - 10m/ OFF - 10m | High | 385 | 5 | High | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 |  | Arunkumar | 2021-10-29
FI_30076 | Flow - Acid Cond. to 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 20000 | kg/hr | -580 | 20580 | D0 | Linear |  |  | Direct | FT_30076 | NoClamp | NONE | NONE | NONE | 23500 | 200 | Low | 7000 | 0.5 | Low | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0022 |  | Arunkumar | 2021-10-29
FI_30536 | Flow - 30E007 Jacket Cooling Wtr | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 300 | m3/hr | -8.7 | 308.7 | D1 | Square Root | 24 |  | Direct | FT_30536 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | 90 | 20/ ON - 2m | High | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0036 |  | Arunkumar | 2021-10-29
FI_30541 | Flow - 30E007 Gas Inlt Air Purge | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 145 | m3/h | -4.205 | 149.205 | D1 | Linear |  |  | Direct | FT_30541 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | 35 | 35 | Urgent | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0022 |  | Arunkumar | 2021-10-29
PDI_30092 | DP - 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | kPa | -2.9 | 102.9 | D2 | Linear |  |  | Direct | PDT_30092 | NoClamp | 100 | 0.5 | Urgent | 65 | 1 | Low | 25 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0027 |  | Arunkumar | 2021-10-29
TI_30094 | Temp - Tailgas ex 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | DegC | -2.9 | 102.9 | D2 | Linear |  |  | Direct | TT_30094 | NoClamp | 100 | 0.5 | Urgent | 36 | 0.5 | High | 20 | 0.5 | High | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0021 |  | Arunkumar | 2021-10-29
TI_30132 | Temp - CWR ex CoolCond(30E007) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 80 | DegC | -2.32 | 82.32 | D2 | Linear |  |  | Direct | TT_30132 | NoClamp | 80 | 0.5 | Urgent | 60 | 0.5 | Low | 20 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0036 |  | Arunkumar | 2021-10-29
TI_30156 | Temp - Acid ex 30C001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | DegC | -2.9 | 102.9 | D2 | Linear |  |  | Direct | TT_30156 | NoClamp | 100 | 0.5 | Urgent | 65 | 0.5 | Low | 30 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0027 |  | Arunkumar | 2021-10-29
PDI_30404 | DP - Filter 30F018 1st stage | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1000 | Pa | -29 | 1029 | D1 | Linear |  |  | Direct | PDT_30404 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
PDI_30405 | DP - Filter 30F018 2nd stage | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1000 | Pa | -29 | 1029 | D1 | Linear |  |  | Direct | PDT_30405 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
PDI_30406 | DP - Filter 30F018 3rd stage | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1000 | Pa | -29 | 1029 | D1 | Linear |  |  | Direct | PDT_30406 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
TI_30160 | 30K001 Enclosure | Q_ANALM | Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | DegC | -2.9 | 102.9 | D2 | Linear |  |  |  |  | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0050 |  | Arunkumar | 2021-10-29
TI_30165 | Temp - 30K001 1st Stage Out | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 60 | DegC | -1.74 | 61.74 | D2 | Linear |  |  | Direct | TT_30165 | NoClamp | 60 | 0.5 | Urgent | 60 | 0.5 | Low | 20 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0050 |  | Arunkumar | 2021-10-29
TI_30168 | Temp - 30K001 2nd Stage Out | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 200 | DegC | -5.8 | 205.8 | D1 | Linear |  |  | Direct | TT_30168 | NoClamp | 200 | 0.5 | Urgent | 159 | 0.5 | Low | 80 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0050 |  | Arunkumar | 2021-10-29
TI_30240 | Temp - NA Comp DE Brg(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 160 | DegC | -4.64 | 164.64 | D1 | Linear |  |  | Direct | TT_30240 | NoClamp | 160 | 0.5 | Urgent | 115 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
TI_30241 | Temp - NA Comp NDE Brg(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 160 | DegC | -4.64 | 164.64 | D1 | Linear |  |  | Direct | TT_30241 | NoClamp | 160 | 0.5 | Urgent | 115 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
TI_30242 | Temp - NA Comp Stg 1 Brg(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 160 | DegC | -4.64 | 164.64 | D1 | Linear |  |  | Direct | TT_30242 | NoClamp | 160 | 0.5 | Urgent | 115 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
TI_30243 | Temp - NA Comp Stg 2 Brg(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 160 | DegC | -4.64 | 164.64 | D1 | Linear |  |  | Direct | TT_30243 | NoClamp | 160 | 0.5 | Urgent | 115 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
TI_30244 | Temp - NA Comp Stg 3 Brg(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 160 | DegC | -4.64 | 164.64 | D1 | Linear |  |  | Direct | TT_30244 | NoClamp | 160 | 0.5 | Urgent | 115 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
TI_30245 | Temp - NA Comp Stg 3 Brg(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 160 | DegC | -4.64 | 164.64 | D1 | Linear |  |  | Direct | TT_30245 | NoClamp | 125 | 0.5 | Urgent | 122 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
TI_30246 | Temp - NA Comp Exp 1 Brg(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 160 | DegC | -4.64 | 164.64 | D1 | Linear |  |  | Direct | TT_30246 | NoClamp | 160 | 0.5 | Urgent | 115 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
TI_30247 | Temp - NA Comp Exp 2 Brg(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 160 | DegC | -4.64 | 164.64 | D1 | Linear |  |  | Direct | TT_30247 | NoClamp | 160 | 0.5 | Urgent | 115 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
TI_30253 | Temp - Mtr Hottest Brg.(30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 120 | DegC | -3.48 | 123.48 | D1 | Linear |  |  | Direct | TT_30253 | NoClamp | 96 | 0.5 | Urgent | 91 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
TI_30254 | Temp - Mtr Hottest Wdg (30K001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 180 | DegC | -5.22 | 185.22 | D1 | Linear |  |  | Direct | TT_30254 | NoClamp | NONE | NONE | NONE | 130 | 10 | Low | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
TI_30257 | Temp - Cool Air 30K001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | DegC | -4.35 | 154.35 | D1 | Linear |  |  | Direct | TT_30257 | NoClamp | 60 | 1 | Urgent | 55 | 1 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
TI_30258 | Temp - Warm Air 30K001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | DegC | -4.35 | 154.35 | D1 | Linear |  |  | Direct | TT_30258 | NoClamp | 120 | 0.5 | Urgent | 80 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
VI_30262A | Vibes - 30K001 stage 1 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30262A | NoClamp | 78 | 0.5 | Urgent | 65 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30262B | Vibes - 30K001 Stage 1 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30262B | NoClamp | 78 | 0.5 | Urgent | 65 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30263A | Vibes - 30K001 stage 2 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30263A | NoClamp | 78 | 0.5 | Urgent | 65 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30263B | Vibes - 30K001 Stage 2 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30263B | NoClamp | 78 | 0.5 | Urgent | 65 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30264A | Vibes - 30K001 3rd stage | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30264A | NoClamp | 60 | 0.5 | Urgent | 50 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30264B | Vibes - 30K001 Stage 3 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30264B | NoClamp | 60 | 0.5 | Urgent | 50 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30265A | Vibes - 30K001 stage 3 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30265A | NoClamp | 60 | 0.5 | Urgent | 50 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30265B | Vibes - 30K001 Stage 3 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30265B | NoClamp | 60 | 0.5 | Urgent | 50 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30266A | Vibes - 30MT02 Stage 1 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30266A | NoClamp | 74 | 0.5 | Urgent | 62 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30266B | TG turbine stage 1 Vibes | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30266B | NoClamp | 74 | 0.5 | Urgent | 62 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30267A | Vibes - 30MT02 Stage 2 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30267A | NoClamp | 74 | 0.5 | Urgent | 62 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
VI_30267B | Vibes - 30MT02 stage 2 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | microns | -4.35 | 154.35 | D1 | Linear |  |  | Direct | VY_30267B | NoClamp | 74 | 0.5 | Urgent | 62 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
ZI_30261A | Vibes - 30K001 Axial | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | -1000 | 1000 | microns | -1058 | 1058 | D0 | Linear |  |  | Direct | ZY_30261A | NoClamp | 700 | 0.5 | Urgent | 500 | 0.5 | Low | -500 | 0.5 | Low | -700 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
ZI_30261B | Vibes - 30K001 Axial | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | -1000 | 1000 | microns | -1058 | 1058 | D0 | Linear |  |  | Direct | ZY_30261B | NoClamp | 700 | 0.5 | Urgent | 500 | 0.5 | Low | -500 | 0.5 | Low | -700 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0060 |  | Arunkumar | 2021-10-29
GI_3001 | Conc - NH3 at NH3 evaporator | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | ppm | -2.9 | 102.9 | D2 | Linear |  |  | Direct | GD_3001 | NoClamp | 50 | 5 | Critical | 25 | 5 | Critical | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  |  |  | Arunkumar | 2021-10-29
GI_3002 | Conc - NH3 at NH3 evaporator | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | ppm | -2.9 | 102.9 | D2 | Linear |  |  | Direct | GD_3002 | NoClamp | 50 | 5 | Critical | 25 | 5 | Critical | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  |  |  | Arunkumar | 2021-10-29
PDI_30007 | DP - NH3 filter 30F004 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 62 | kPa | -1.798 | 63.798 | D2 | Linear |  |  | Direct | PDT_30007 | NoClamp | 50 | 0.5 | Urgent | 40 | 0.5 | Low | -10 | 0.5 | Low | -10 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0005 |  | Arunkumar | 2021-10-29
PDI_30291 | DP - NH3 Filter 30F003B | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 60 | kPa | -1.74 | 61.74 | D2 | Linear |  |  | Direct | PDT_30291 | NoClamp | NONE | NONE | NONE | 50 | 5 | Low | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0006 |  | Arunkumar | 2021-10-29
TI_30004 | Temp - NH3 evap 30E001 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | -50 | 75 | DegC | -53.625 | 78.625 | D1 | Linear |  |  | Direct | TT_30004 | NoClamp | NONE | NONE | NONE | 50 | 0.5 | Low | 10 | 0.5 | Low | -20 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0005 |  | Arunkumar | 2021-10-29
AI_30145 | Conduc - StmCondy ex NA(30T096) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | uS | -2.9 | 102.9 | D2 | Linear |  |  | Direct | AT_30145 | NoClamp | 90 | 15 | Urgent | 75 | 5 | Low | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0030 |  | Arunkumar | 2021-10-29
TI_30378 | Temp - NH3/ AIR Mix to NA Reac. | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 300 | DegC | -8.7 | 308.7 | D1 | Linear |  |  | Direct | TT_30378 | NoClamp | NONE | NONE | NONE | 260 | 10 | High | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 |  | Arunkumar | 2021-10-29
TI_30381 | Temp - NA Reactor 30R012 Exit | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 600 | DegC | -17.4 | 617.4 | D1 | Linear |  |  | Direct | TT_30381 | NoClamp | 440 | 5 | Urgent | 415 | 0/ ON - 10m/ OFF - 10m | High | 385 | 5 | High | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0016 |  | Arunkumar | 2021-10-29
TI_30411 | Temp - 30E012 NOx Inlet | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 500 | DegC | -14.5 | 514.5 | D1 | Linear |  |  | Direct | TT_30411 | NoClamp | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0021 |  | Arunkumar | 2021-10-29
TI_30473 | Temp - 30E006 NOx Inlet | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 600 | DegC | -17.4 | 617.4 | D1 | Linear |  |  | Direct | TT_30473 | NoClamp | NONE | NONE | NONE | 320 | 5 | High | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | (HOLD) |  | QN-VT-30-D-0021 |  | Arunkumar | 2021-10-29
PDI_30209 | DP - Boiler Circ.Pmps(30P005A/B) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 600 | kPa | -17.4 | 617.4 | D1 | Linear |  |  | Direct | PDT_30209 | NoClamp | 600 | 0.5 | Urgent | 500 | 0.5 | High | 30 | 0.5 | High | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0046 |  | Arunkumar | 2021-10-29
TI_30112 | Temp - BFW from 30E006 | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 100 | 300 | DegC | 94.2 | 305.8 | D1 | Linear |  |  | Direct | TT_30112 | NoClamp | 300 | 0.5 | Urgent | 250 | 0.5 | Low | 200 | 0.5 | Low | 100 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0021 |  | Arunkumar | 2021-10-29
AI_30134 | Conc(O2) -Gas ex AbsCol(30C001) | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 30 | % | -0.87 | 30.87 | D2 | Linear |  |  | Direct | AT_30134 | NoClamp | 21 | 0.05/ ON-10s | High | 4 | 0.2/ ON - 10s | Low | NONE | NONE | NONE | 0 | 0.05 | High |  |  |  |  | (HOLD) |  | QN-VT-30-D-0100 |  | Arunkumar | 2021-10-29
PI_30060 | Press - TG turbine outlet | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 8 | kPag | -0.232 | 8.232 | D3 | Linear |  |  | Direct | PT_30060 | NoClamp | 8 | 0.5 | Urgent | 6 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0010 |  | Arunkumar | 2021-10-29
PI_30170 | Press - 30MT02 interstage | Q_ANALM | HW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 600 | kPag | -17.4 | 617.4 | D1 | Linear |  |  | Direct | PT_30170 | NoClamp | 600 | 0.5 | Urgent | 460 | 0.5 | Low | 0 | 0.5 | Low | 0 | 0.5 | Urgent |  |  |  |  | (HOLD) |  | QN-VT-30-D-0012 |  | Arunkumar | 2021-10-29
HIC_30075_L | Primary to Sec. Air Let Down Output Alarm | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  |  | HIC_30075.AUTOMANA.OP | NoClamp | 95 | 0.5 | (HOLD) | 90 | 0.5 | (HOLD) | 10 | 0.5 | (HOLD) | 5 | 0.5 | (HOLD) |  |  |  |  | NONE |  | QN-VT-30-D-0011 | C&I Sheet:48 | Arunkumar | 2021-10-29
Note on S72: V, Vidya Sneha: No connection
Note on S77: V, Vidya Sneha: No connection
Note on S89: V, Vidya Sneha: No AI
Note on K130: V, Vidya Sneha: EU filled from Module as missing in report

## APP A.7 - Analogue Controllers
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | EU Range Low | EU Range High | Eng Units | PV Ext Range Low | PV Ext Range High | PV Format | PV Char | Low cutoff | Filter Time | Input Direction | PV Clamping | PV Source Tag | SP Source Tag | SP | SP Ramprate | SP Low Limit | SP High Limit | PV Tracking | Sec Init Option | Normal Mode | OP Low Limit | OP High Limit | Bad Ctrl OP | OP Destination Tag | OP Direction | Control Action | Gain (%/%) | Integral (Minutes) | Derivative (Minutes) | Safety Interlock | Safe OP | PV High High Value | PV High High DB | PV High High Priority | PV High Value | PV High DB | PV High Priority | PV Low Value | PV Low DB | PV Low Priority | PV Low Low Value | PV Low Low DB | PV Low Low Priority | ROC Pos Value | ROC Pos Priority | ROC Neg Value | ROC Neg Priority | OP High Value | OP High Priority | OP Low Value | OP Low Priority | Dev High Value | Dev High Prioritiy | Dev Low Value | Dev Low Priority | Bad PV Priority | Alarm Disable | P&ID | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
LIC_30101 | Level - AN cond. (30D010) | Q_PID | PID with Fanout | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | NoClamp | LT_30101 |  | 60 |  | 0 | 100 | No | No | Auto | 0 | 100 | SHEDHOLD |  |  | Reverse | 6.21 | 9.02 | 0 |  |  | 95 | 0.5 | Urgent | 90 | 0.5 | Low | 30 | 0.5 | Low | 15 | 0.5 | Urgent | [12 empty] | (HOLD) |  | QN-VT-30-D-0029 | C&I Sheet:1A & 4 | Arunkumar | 2021-09-10
LY_30101A | Level - AN cond. (30D010) | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 100 |  | LV_30101A | Direct | [32 empty] | QN-VT-30-D-0029 | C&I Sheet:1A & 4 | Arunkumar | 2021-09-15
LY_30101B | Level - AN cond. (30D010) | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 100 |  | LV_30101B | Direct | [32 empty] | QN-VT-30-D-0029 | C&I Sheet:1A & 4 | Arunkumar | 2021-09-15
LIC_30002 | Level - NH3 Evap. 30E001 | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | NoClamp | LT_30002 |  | 50 |  | 0 | 100 | No | No | Auto | 0 | 100 | SHEDHOLD | LV_30002 | Direct | Reverse | 4.146 | 8.209 | 0 | C&I Sheet:1B & 5 | 0 | 70 | 0.5 | Urgent | 60 | 3 | Low | 35 | 3 | Low | -5 | 0.5 | Urgent | [12 empty] | (HOLD) |  | QN-VT-30-D-0005 | C&I Sheet:1B & 5 | Arunkumar | 2021-09-15
PIC_30006 | Press - NH3 gas ex 30E001 | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | kPag | -58 | 2058 | D0 | Linear |  |  | Direct | NoClamp | PT_30006 |  | 1200 | 4 | 0 | 2000 | No | No | Auto | 0 | 100 | SHEDHOLD | PV_30006 | Direct | Reverse | 1.9 | 2.913 | 0 | C&I Sheet:1B & 5 | 0 | 2000 | 0.5 | Urgent | 1300 | 0.5 | Low | 900 | 0.5 | Low | -20 | 0.5 | Urgent | [12 empty] | (HOLD) |  | QN-VT-30-D-0005 | C&I Sheet:1B & 6 | Arunkumar | 2021-09-15
LIC_30090 | Abs.Tower 30C001 | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | NoClamp | LT_30090 |  | 50 |  | 0 | 100 | No | No | Auto | 0 | 100 | SHEDHOLD | LV_30090 | Direct | Direct | 6.08 | 4.1 | 0 | C&I Sheet:1E & 11 | 0 | 95 | 0.5 | Urgent | 70 | 0.5 | Low | 20 | 0.5 | Low | 10 | 0.5 | Urgent | [12 empty] | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet:1E & 11 | Arunkumar | 2021-09-15
LIC_30118 | Level - Cond. 30D009 | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | NoClamp | LT_30118 |  | 60 |  | 0 | 100 | No | No | Auto | 0 | 100 | SHEDHOLD | LV_30118 | Direct | Direct | 15 | 3 | 0 |  |  | 95 | 0.5 | Urgent | 80 | 0.5 | Low | 30 | 0.5 | Low | 15 | 0.5 | Urgent | [12 empty] | (HOLD) |  | QN-VT-30-D-0030 | C&I Sheet:1H & Simple PID | Arunkumar | 2021-09-15
PIC_30387A | Press - NA MP Steam Export | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 5400 | kPa | -156.6 | 5556.6 | D0 | Linear |  |  | Direct | NoClamp | PT_30387 |  | 3800 | 7 | 0 | 4400 | No | No | Auto | 0 | 100 | SHEDSAFE | PV_30387A | Reverse | Direct | 2 | 1 | 0 |  | 0 | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0005 | C&I Sheet:1I & Simple PID | Arunkumar | 2021-10-29
PIC_30387B | Press - NA Plant MP Steam Vent | Q_PID | PID with HW AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 5400 | kPag | -156.6 | 5556.6 | D0 | Linear |  |  | Direct | NoClamp | PIC_30387.DACA.PV |  | 4090 |  | 0 | 4400 | No | No | Auto | 0 | 100 | SHEDHOLD | PV_30387B | Direct | Direct | 4 | 0.5 | 0 | C&I Sheet:1I, 21 & 22 | C&I Sheet:1I, 21 & 22 | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0005 | C&I Sheet:1I, 21 & 22 | Arunkumar | 2021-10-29
LIC_30070 | Level - Cooler-Cond. (30E007) | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | NoClamp | LT_30070 |  | 40 |  | 0 | 100 | No | No | Auto | 0 | 100 | SHEDHOLD | LV_30070 | Direct | Direct | 0.345 | 2.375 | 0 |  |  | 90 | 0.5 | Urgent | 70 | 0.5 | Low | 30 | 0.5 | Low | 10 | 10 | Urgent | [12 empty] | (HOLD) |  | QN-VT-30-D-0022 | C&I Sheet:Simple PID | Arunkumar | 2021-10-29
LIC_30361 | Level - Condenser Receiver 30T010 | Q_PID | PID with Fanout | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | NoClamp | LT_30361 |  | 40 |  | 0 | 100 | No | No | Auto | 0 | 100 | NOSHED |  |  | Direct | 1.324 | 4 | 0 |  |  | NONE | NONE | NONE | 50 | 2 | High | 15 | 2 | Low | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0090 | C&I Sheet:1K & 24 | Arunkumar | 2021-10-29
LY_30361 | Level- Condenser Receiver 30T010 | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 100 |  | LV_30361 | Reverse | [32 empty] | QN-VT-30-D-0090 | C&I Sheet:1K & 24 | Arunkumar | 2021-10-29
LY_30306A | Level – Recirc. Condenser 30T010 | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 100 |  | LV_30306A | Direct | [32 empty] | QN-VT-30-D-0090 | C&I Sheet:1K & 24 | Arunkumar | 2021-10-29
LY_30306B | Level – Drain Condenser 30T010 | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 100 |  | LV_30306B | Reverse | [32 empty] | QN-VT-30-D-0090 | C&I Sheet:1K & 24 | Arunkumar | 2021-10-29
TIC_30068 | Temp - Econ. Outlet (30E006) | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 300 | DegC | -8.7 | 308.7 | D1 | Linear |  |  | Direct | NoClamp | TT_30068 |  | 180 |  | 0 | 260 | Yes | No | Auto | 0 | 100 | SHEDSAFE | TV_30068 | Direct | Reverse | 3.276 | 43.627 | 0 | C&I Sheet:29 | 0 | 270 | 1 | Urgent | 222 | 2 | High | 175 | 2 | High | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0021 | C&I Sheet:1M & 29 | Arunkumar | 2021-10-29
FIC_30082 | Flow - Sec. Air to 30C001 | Q_PID | PID with HW AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 21000 | kg/hr | -609 | 21609 | D0 | Linear |  |  |  | NoClamp | FI_30080.DACA.PV |  | 14500 |  | 0 | 21000 | Yes | No | Auto | 0 | 100 | SHEDHOLD | HV_30082 | Direct | Reverse | 0.065 | 2 | 0 | C&I Sheet:30 | C&I Sheet:30 | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0021 | C&I Sheet:1N & 30 | Arunkumar | 2021-10-29
TIC_30081 | Temp - Secondary Air to Absorber | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 150 | DegC | -4.35 | 154.35 | D1 | Linear |  |  |  | NoClamp | TI_30081.DACA.PV |  | 70 |  | 0 | 100 | Yes | No | Auto | 0 | 100 | SHEDHOLD | TV_30081 | Direct | Reverse | 0.5 | 3 | 0 | C&I Sheet:30 | 0 | NONE | NONE | NONE | 120 | 30 | High | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | NONE |  | QN-VT-30-D-0021 | C&I Sheet:1N & 30 | Arunkumar | 2021-10-29
TIC_30235 | Temp - Tailgas to Mixer (30N002) | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 400 | DegC | -11.6 | 411.6 | D1 | Linear |  |  | Direct | NoClamp | TT_30235 |  | 350 |  | 0 | 400 | No | No | Auto | 0 | 100 | SHEDHOLD | TV_30235 | Reverse | Direct | 0.942 | 1.93 | 0 |  |  | NONE | NONE | NONE | 375 | 15 | Urgent | 335 | 5 | High | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0021 | C&I Sheet: Simple PID | Arunkumar | 2021-10-29
PIC_30083A_CM | Press - 30K010 Discharge SP | Q_PID | PID with HW AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1400 | kPa | -40.6 | 1440.6 | D0 | Linear |  |  |  | NoClamp | PI_30152.DACA.PV |  | 960 |  | 0 | 1000 | No | No | Auto | 0 | 100 | NOSHED | PIC_30083A | Direct | Reverse | 0.1 | 0.2 | 0 |  |  | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | NONE |  | QN-VT-30-D-0013 | C&I Sheet: Simple PID | Arunkumar | 2021-10-29
TIC_30274 | Temp - Lube Oil (30K001) | Q_PID | PID with HW AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | DegC | -2.9 | 102.9 | D2 | Linear |  |  |  | NoClamp | TT_30274 - SIS |  | 40 |  | 0 | 100 | No | No | Auto | 0 | 100 | SHEDHOLD | TV_30274 | Direct | Reverse | 1.996 | 0.701 |  |  |  | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0070 | C&I Sheet: Simple PID | Arunkumar | 2021-10-29
TIC_30096 | Temp - Tailgas ex 30E011 | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 100 | 200 | DegC | 97.1 | 202.9 | D2 | Linear |  |  | Direct | NoClamp | TT_30096 |  | 140 |  | 100 | 200 | No | No | Auto | 0 | 100 | SHEDHOLD | TV_30096 | Reverse | Reverse | 1 | 1.5 | 16 |  |  | 195 | 0.5 | Urgent | 150 | 0.5 | Low | 120 | 0.5 | Low | 5 | 0.5 | Urgent | [12 empty] | (HOLD) |  | QN-VT-30-D-0021 | C&I Sheet: PID_Interlock | Arunkumar | 2021-10-29
LIC_30390 | Level - NA Steam Drum (30D004) | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  | Direct | NoClamp | LT_30390 |  | 50 |  | 0 | 65 | No | No | Auto | 0 | 100 | NOSHED | LV_30390 | Direct | Reverse | 5 | 7 | 0 |  |  | NONE | NONE | NONE | 65 | 2 | High | 43 | 2 | High | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0032 | C&I Sheet: PID_Interlock | Arunkumar | 2021-10-29
PIC_30225 | Press - TG to Expander (30MT02) | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | kPag | -58 | 2058 | D0 | Linear |  |  |  | NoClamp | PY_30255.DACA.PV |  | 770 |  | 0 | 770 | No | No | Auto | 0 | 100 | SHEDHOLD | PV_30225 | Reverse | Direct | 13.963 | 6.124 | 0 |  |  | NONE | NONE | NONE | 910 | 10 | Urgent | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0012 | C&I Sheet: Simple PID | Arunkumar | 2021-10-29
AIC_30091A | Conc(NA) - NA ex AbsCol (30C001) | Q_PID | PID | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 100 | % | -2.9 | 102.9 | D2 | Linear |  |  |  | NoClamp | AI_30091A.DACA.PV |  | 59.3655 |  | 0 | 100 | Yes | No | Auto | 0 | 10000 | SHEDHOLD |  |  | Direct | 14.24 | 71.36 | 0 |  |  | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0027 | C&I Sheet:1E & 31 | Arunkumar | 2021-10-29
FIC_30109 | Process Water to 30C001 | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 10000 | kg/hr | -290 | 10290 | D0 | Linear |  |  | Direct | NoClamp | FT_30109 | C&I Sheet:31 | 5800 |  | 0 | 10000 | Yes | No | Cas | 0 | 100 | SHEDHOLD | FV_30109 | Direct | Reverse | 0.031 | 0.066 | 0 | C&I Sheet:31 | 0 | NONE | NONE | NONE | NONE | NONE | NONE | 2000 | 200/ ON-1M | Low | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0029 | C&I Sheet:1E & 31 | Arunkumar | 2021-10-29
FIC_30024 | Flow - 30K001 Primary Air Flow | Q_PID | PID with HW AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 120000 | kg/hr | -3480 | 123480 | D0 | Linear |  |  |  | NoClamp | FTY30037.DACA.PV |  | 99000 |  | 0 | 100000 | Yes | No | Cas | 0 | 100 | SHEDHOLD | HV_30024 | Direct | Reverse | 0.247 | 0.068 |  | C&I Sheet:32 | C&I Sheet:32 | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0012 | C&I Sheet:1L & 32 | Arunkumar | 2021-10-29
HIC_30030 | SP - Blow-off 30K001 | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Man | 0 | 100 |  | HV_30030 | Reverse |  |  |  |  | C&I Sheet: HIC Controller | 100 | [26 empty] | QN- VT- 30-D-0011 | C&I Sheet: HIC Controller | Arunkumar | 2021-10-29
HIC_30198 | SP - Continuous Blowdown 30D004 | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Man | 0 | 100 |  | HV_30198 | Direct |  |  |  |  | C&I Sheet: HIC Controller | 0 | [26 empty] | QN-VT-30-D-0032 | C&I Sheet: HIC Controller | Arunkumar | 2021-10-29
HIC_30143 | SP - TG Turbine IGV | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Man | 0 | 100 |  | HV_30143 | Reverse |  |  |  |  | C&I Sheet: HIC Controller | 8 | [26 empty] | QN-VT-30-D-0012 | C&I Sheet: HIC Controller | Arunkumar | 2021-10-29
HIC_30311 | Secondary Air to TG Htr1(30E010) | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Man | 0 | 100 |  | HV_30311 | Reverse | [32 empty] | QN- VT- 30-D-0021 | C&I Sheet: HIC Controller | Arunkumar | 2021-10-29
PIC_30025 | Press - 30K001 discharge | Q_PID | PID with Fanout | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 2000 | kPag | -58 | 2058 | D0 | Linear |  |  |  | NoClamp | PT_30025 - SIS |  | 0 |  | 0 | 2000 | No | No | Auto | 0 | 100 | SHEDHOLD |  |  | Direct | 4 | 1 | 0 | C&I Sheet:39 | C&I Sheet:39 | 1060 | 0.5 | Urgent | 1000 | 0.5 | Low | 400 | 0.5 | Low | 300 | 0.5 | Urgent | [12 empty] | (HOLD) |  | QN-VT-30-D-0012 | C&I Sheet:1L & 39 | Arunkumar | 2021-10-29
PY_30025A | Press - 30K001 discharge | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 100 |  | PV_30025A | Direct | [32 empty] | QN-VT-30-D-0012 | C&I Sheet:1L & 39 | Arunkumar | 2021-10-29
PY_30025B | Press - 30K001 discharge | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 100 |  | PV_30025B | Direct | [32 empty] | QN-VT-30-D-0012 | C&I Sheet:1L & 39 | Arunkumar | 2021-10-29
PIC_30426 | Press - NA Steam Drum | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 6000 | kPa | -174 | 6174 | D0 | Linear |  |  |  | NoClamp | PT_30426 |  | 4199.374 | 15 | 0 | 4400 | Yes | No | Auto | 0 | 100 | SHEDSAFE | PV_30426 | Direct | Reverse | 2.8 | 1.5 | 0 | C&I Sheet:40 | 0 | NONE | NONE | NONE | 4900 | 50 | High | 4000 | 50 | High | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0032 | C&I Sheet:1L & 40 | Arunkumar | 2021-10-29
TIC_30384 | Temp - NA MP Steam Export | Q_PID | PID with Fanout | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 500 | DegC | -14.5 | 514.5 | D1 | Linear |  |  |  | NoClamp | TT_30384 |  | 425 |  | 0 | 445 | Yes | No | Auto | 0 | 100 | SHEDSAFE |  |  | Reverse | 2.681 | 0.515 |  |  | 50 | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0032 | C&I Sheet:1L & 41 | Arunkumar | 2021-10-29
TY_30384A | Temp - NA MP Steam Export | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 100 |  | TV_30384A | Direct | [32 empty] | QN-VT-30-D-0032 | C&I Sheet:1L & 41 | Arunkumar | 2021-10-29
TY_30384B | Temp - NA MP Steam Export | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Cas | 0 | 88 |  | TV_30384B | Direct | [32 empty] | QN-VT-30-D-0032 | C&I Sheet:1L & 41 | Arunkumar | 2021-10-29
AIC_30051 | Conc - NOx in NA Tailgas | Q_PID | PID | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1200 | ppm | -34.8 | 1234.8 | D0 | Linear |  |  |  | NoClamp | AIC_30051.DACA.PV |  | 80 | 1 | 0 | 100 | No | No | Auto | 0 | 40 | SHEDHOLD |  |  | Direct | 0.75 | 1.3 |  | C&I Sheet: 42 | C&I Sheet: 42 | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0015 | C&I Sheet:1P & 42 | Arunkumar | 2021-10-29
FIC_30051 | Flow - NH3 gas to 30R003 | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 60 | kg/hr | -1.74 | 61.74 | D2 | Square Root | 4.8 |  |  | NoClamp | FT_30051 |  | 4.6977 |  | 0 | 40 | Yes | No | Cas | 0 | 100 | SHEDHOLD | FV_30051 | Direct | Reverse | 0.3 | 0.2 | 0 | C&I Sheet: 42 | -3.3 | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0015 | C&I Sheet:1O & 42 | Arunkumar | 2021-10-29
HIC_30075 | Primary to Sec. Air Let Down | Q_AM | Automan with AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | [19 empty] | Man | 0 | 100 |  | HV_30075 | Direct |  |  |  |  | C&I Sheet:48 | C&I Sheet:48 | [24 empty] | (HOLD) |  | QN-VT-30-D-0011 | C&I Sheet:48 | Arunkumar | 2021-10-29
FIC_30074 | Flow - Secondary Air to Primary | Q_PID | PID with HW AI/AO | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 6000 | kg/hr | -174 | 6174 | D2 | Square Root | 480 |  |  | NoClamp | FT_30074 |  | 0 |  | 0 | 3000 | Yes | No | Auto | 0 | 100 | NOSHED | FV_30074 | Direct | Reverse | 0.3 | 0.02 | 0 | C&I Sheet:49 | C&I Sheet:49 | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | [12 empty] | (HOLD) |  | QN-VT-30-D-0011 | C&I Sheet:49 | Arunkumar | 2021-10-29
Note 1 : PID Equation B is used for all controllers
Note 2: For All SIS tags please refer App.D SM_DCS Interface List for exact parameter name

## APP A.8 - Internal Analogs
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Main Function Block | Asset | Ass Display | Controller | Location | EU Range Low | EU Range High | Eng Units | PV Ext Range Low | PV Ext Range High | PV Format | PV Source Tag | SP Source Tag | SP Low Limit | SP High Limit | PV Tracking | Normal Mode | OP Low Limit | OP High Limit | Bad Ctrl OP | Direction | Control Action | Gain (%/%) | Integral (Minutes) | Derivative (Minutes) | Process Interlock | Shutdown Interlock | Safe OP | PV High High Value | PV High High Priority | PV High Value | PV High Priority | PV Low Value | PV Low Priority | PV Low Low Value | PV Low Low Priority | OP High Value | OP High Priority | OP Low Value | OP Low Priority | Dev High Value | Dev High Prioritiy | Dev Low Value | Dev Low Priority | Bad PV Priority | Alarm Disable | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
Non Identified

## APP A.9 - Logic Control Mod
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
A30P008AB_L | Elec - Acid Condy Pump (30P008A/B) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 3 | Arunkumar | 2021-09-15
LIC_30101_L | Level - AN cond. (30D010) Fanout Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 4 | Arunkumar | 2021-09-15
LIC_30002_L | Level - NH3 Evap. 30E001 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 5 | Arunkumar | 2021-09-15
PIC_30006_L | Press - NH3 gas ex 30E001 Alarm Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 6 | Arunkumar | 2021-09-15
PI_30272_L | Press - Lube oil 30K001 Alarm Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 7 | Arunkumar | 2021-09-15
A30P002_L | Elec - NA Lube Oil Pump(30P002) Interlock Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 7 | Arunkumar | 2021-09-15
A30KEH1_L | Elec - NA Comp Oil Htr (30KEH1) Interlock Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 8 | Arunkumar | 2021-09-15
XN_30140_L | Air to 30MT02 Interlock Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 9 | Arunkumar | 2021-09-15
XN_30297_L | Inst. Air to 30MT02 Interlock Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 10 | Arunkumar | 2021-09-15
LIC_30090_L | Abs.Tower 30C001 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 11 | Arunkumar | 2021-09-15
XN_30288_L | Nitric Acid ex 30C001 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 12 | Arunkumar | 2021-09-15
A30P014_L | Elec - Drip Acid Pump (30P014) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 13 | Arunkumar | 2021-09-15
A30P021_L | Elec - Waste Water Pump (30P021) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 14 | Arunkumar | 2021-09-15
A30P012A_L | Elec - BFW Pump 30P012A | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 15 | Arunkumar | 2021-10-29
A30P012B_L | Elec - BFW Pump 30P012B | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 16 | Arunkumar | 2021-10-29
A30P005A_L | Elec -Emergency BFW Pump 30P005A Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 17 | Arunkumar | 2021-10-29
A30P005B_L | Elec -Emergency BFW Pump 30P005B Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 18 | Arunkumar | 2021-10-29
BFW_PMP_L | BFW Pumps Alarm Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 19 | Arunkumar | 2021-10-29
A30P009AB_L | Elec - NA Stm Condy Pmp (30P009A/B) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 20 | Arunkumar | 2021-10-29
PIC_30387AB_L | Press - NA Plant MP Steam Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 21 & 22 | Arunkumar | 2021-10-29
A38P001AB_L | Elec - NA Storage Pump (38P001A/B) | STD_CM | Control Standalone | AREA30 | FT_30222+T30:W30 | CPM_MCC2_01 | MCC2 | C&I Sheet: 23 | Arunkumar | 2021-10-29
LIC_30361_L | Level - Condenser Reciever 30T010 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 24 | Arunkumar | 2021-10-29
A30P004AB_L | Elec-Sec Air Cond. Pumps 30P004A/B Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 25 HS_30334A and HS_30336A HW Tags | Arunkumar | 2021-10-29
FFY_30017 | NH3 – Air Ratio Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 1L & 26 | Arunkumar | 2021-10-29
XV_30280_L | Seal Gas 30MT02 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 27 | Arunkumar | 2021-10-29
TIC_30068_L | Temp - Econ. Outlet (30E006) | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 29 | Arunkumar | 2021-10-29
FIC_30082_L | Flow - Sec. Air to 30C001 | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 30 | Arunkumar | 2021-10-29
FI_30080_L | Sec. Air to 30C001 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 30 | Arunkumar | 2021-10-29
ZAL_30082_L | Secondary Air to 30C001 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 30 | Arunkumar | 2021-10-29
TIC_30081_L | Temp - Secondary Air to Absorber | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 30 | Arunkumar | 2021-10-29
XN_30056_L | NOx Stream 1 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 27 | Arunkumar | 2021-10-29
TI_30054_L | Temp - TG to SCR Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 27 & 28 | Arunkumar | 2021-10-29
I_30_03 | I_30_03 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 28 | Arunkumar | 2021-10-29
PIC_30083A_L | Press - 30K010 Discharge SP Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: Simple PID Logic | Arunkumar | 2021-10-29
HS_30328_L | 30K010 Load Load Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: Simple PID Logic | Arunkumar | 2021-10-29
FIC_30109_L | Process Water to 30C001 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 31 | Arunkumar | 2021-10-29
AIC_30091A_L | Conc(NA) - NA ex AbsCol (30C001) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 31 | Arunkumar | 2021-10-29
FI_30091A_L | Flow - Acid Vol Flow ex 30C001 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 31 | Arunkumar | 2021-10-29
LIC_30390_L | Level - NA Steam Drum (30D004) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: PID_Interlock Logic | Arunkumar | 2021-10-29
FIC_30024_L | Flow - 30K001 Primary Air Flow Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 32 | Arunkumar | 2021-10-29
ZAH_30024_L | Position -IGV Error -FIC in MAN Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 32 | Arunkumar | 2021-10-29
FIC_30024_SP_RAMP | Flow - 30K001 Primary Air Flow Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 33 | Arunkumar | 2021-10-29
AI_30091A_L | Conc(NA) - NA ex AbsCol (30C001) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 34 | Arunkumar | 2021-10-29
TI_30379_L | Temp - NA Catalyst Gauze 30R012 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 35 TY_30379 HW Tag | Arunkumar | 2021-10-29
HIC_30030_L | SP - Blow-off 30K001 Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: HIC Controller | Arunkumar | 2021-10-29
A30K001_L | Elec - NA Compressor (30K001) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 36 | Arunkumar | 2021-10-29
II_30249_L | Amps - 30K001 Motor Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 36 | Arunkumar | 2021-10-29
A30P007AB_L | Elec - Acid Condy Pump (30P007A/B) Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 37 | Arunkumar | 2021-10-29
A30P010B_L | Elec - 2ndyAir LO Aux Pump-30P010B Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 38 HS_30333A HW Tag | Arunkumar | 2021-10-29
PIC_30025_L | Press - 30K001 discharge Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 39 | Arunkumar | 2021-10-29
PIC_30426_L | Press - NA Steam Drum Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 40 | Arunkumar | 2021-10-29
TIC_30384_L | Temp - NA MP Steam Export Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 41 | Arunkumar | 2021-10-29
AI_30067_L | AT_30067 Analyser Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 43 & 44 | Arunkumar | 2021-10-29
AI_30067F_L | Conc(NOx) -TailGas to Stack Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 44 | Arunkumar | 2021-10-29
AI_30067A_B_L | Conc - NO from NA Plant Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 45 | Arunkumar | 2021-10-29
AI_30067C_D_L | Conc - NO2 from NA Plant Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 45 | Arunkumar | 2021-10-29
AI_30067E_H_L | AT_30067H - N2O from NA Plant Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 45 | Arunkumar | 2021-10-29
AI_30067F_G_L | Conc - NOx from NA Plant Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 45 | Arunkumar | 2021-10-29
AQI_30067FG_L | Conc - AVG NOX in NA Tailgas Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 47 | Arunkumar | 2021-10-29
HIC_30075_L | Primary to Sec. Air Let Down Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 48 | Arunkumar | 2021-10-29
FIC_30074_L | Flow - Secondary Air to Primary Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 49 | Arunkumar | 2021-10-29
AI_30056_L | Conc (NOx) -TailGas Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 50 | Arunkumar | 2021-10-29
AI_30133_L | Service Switch - NA CW Return pH Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 51 | Arunkumar | 2021-10-29
FTY_30319 | Stack Flow Calculation | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 52 | Arunkumar | 2021-10-29
HS_30322 | Sec. Air Comp Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: 53 HS_30322A/B/C/D HW Tags | Arunkumar | 2021-10-29
FY_30063_L | Flow - 30K001 Total Air Flow Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: Misc Calculation | Arunkumar | 2021-10-29
PI_CALCS | Miscellaneous Calculation | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: Misc Calculation | Arunkumar | 2021-10-29
NH3_RESET_DCS | Ammonia Reset Logic | STD_CM | Control Standalone | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | C&I Sheet: SIS Logic ZY_30017 HW Tag | Arunkumar | 2021-10-29

## APP A.10 - Misc
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
None Identified

## APP A.12 - Deviation Alarm
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | EU Range Low | EU Range High | Eng Units | PV Ext Range Low | PV Ext Range High | PV Format | PV Char | Input Direction | PV Source Tag A | PV Source Tag B | PV Clamping | PV High High Value | PV High High DB | PV High High Priority | PV High Value | PV High DB | PV High Priority | PV Low Value | PV Low DB | PV Low Priority | PV Low Low Value | PV Low Low DB | PV Low Low Priority | ROC Pos Value | ROC Pos Priority | ROC Neg Value | ROC Neg Priority | Bad PV Priority | Alarm Disable | P&ID | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
FDA_30017 | Flow - FT_30017 / FT_30018 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 500 | kg/hr | -14.5 | 514.5 | D1 | Linear | Direct | FTY_30017_L.AIREF.PV | FT_30018 - SIS | NoClamp | NONE | NONE | NONE | 150 | 5/ ON - 30s | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 39 | Arunkumar | 2021-10-29
FDA_30037 | Flow - FT_30037 / FT_30036 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1500 | kg/hr | -43.5 | 1543.5 | D0 | Linear | Direct | FTY_30037.DACA.PV | FTY_30036 - SIS | NoClamp | NONE | NONE | NONE | 1200 | 60/ ON-20s | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0011 | C&I Sheet: 39 | Arunkumar | 2021-10-29
PDA_30014 | Press - PT_30014 / PT_30015 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 25 | kPag | -0.725 | 25.725 | D2 | Linear | Direct | PI_30014.DACA.PV | PT_30015 - SIS | NoClamp | NONE | NONE | NONE | 20 | 1 | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 39 | Arunkumar | 2021-10-29
PDA_30033 | Press - PT_30033 / PT_30034 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 25 | kPag | -0.725 | 25.725 | D2 | Linear | Direct | PI_30033.DACA.PV | PT_30034 - SIS | NoClamp | NONE | NONE | NONE | 20 | 1 | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0011 | C&I Sheet: 39 | Arunkumar | 2021-10-29
TDA_30013 | Temp - TT_30013 / TT_30016 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 3 | DegC | -0.087 | 3.087 | D3 | Linear | Direct | TI_30013.DACA.PV | TT_30016 - SIS | NoClamp | NONE | NONE | NONE | 1.5 | 0.1 | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 39 | Arunkumar | 2021-10-29
TDA_30032 | Deviation - TT_30032 / TT_30035 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 5 | DegC | -0.145 | 5.145 | D3 | Linear | Direct | TI_30032.DACA.PV | TT_30035 - SIS | NoClamp | NONE | NONE | NONE | 3 | 0.15 | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0011 | C&I Sheet: 39 | Arunkumar | 2021-10-29
FDA_30021 | Flow Dev - FT_30017 / FT_30021 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 500 | kg/hr | -14.5 | 514.5 | D1 | Linear | Direct | FTY_30017.DACA.PV | FI_30021.DACA.PV | NoClamp | NONE | NONE | NONE | 150 | 5 | High | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0010 | C&I Sheet: 39 | Arunkumar | 2021-10-29
ADA_30051 | Conc - PPM Diff for AIC30051 (Abs) | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 25 | ppm | -0.725 | 25.725 | D2 | Linear | Direct | AI_30067F_G.DACA.PV | AIC_30051.PIDA.SP | NoClamp | NONE | NONE | NONE | 20 | 1/ON-20M/OFF-10M | High | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0015 | C&I Sheet: 39 | Arunkumar | 2021-10-29
ADA_30051 | Conc - PPM Diff for AIC30051 (High) | DACAB | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 25 | ppm | -0.725 | 25.725 | D2 | Linear | Direct | AI_30067F_G.DACA.PV | AIC_30051.PIDA.SP | NoClamp | NONE | NONE | NONE | 20 | 1/ ON-30M/OFF-1M | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0015 | C&I Sheet: 39 | Arunkumar | 2021-10-29
TDI_30378 | Temp - TT_30378 / TY_30379 | Q_ANALM | SW Analogue Indicator With Alarming | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | 0 | 1100 | kg/hr | -31.9 | 1131.9 | D0 | Linear | Direct | TI_30378.DACA.PV | TI_30379.DACA.PV | NoClamp | NONE | NONE | NONE | 720 | 5 | Urgent | NONE | NONE | NONE | NONE | NONE | NONE |  |  |  |  | NONE |  | QN-VT-30-D-0016 | C&I Sheet: 39 | Arunkumar | 2021-10-29
Note: For All SIS tags please refer App.D SM_DCS Interface List for exact parameter name

## APP A.11 PT FlowComp
PCS Tag Name | PCS Description | Control Strategy | Control Strategy Description | Asset | Ass Display | Controller | Location | PV Source | Temp. Source | Press. Source | PV Eqn | PV Char - FlowComp | Comp Low Lmt | Comp High Lmt | Reference Temp | Reference Pressure | EU Range Low | EU Range High | Eng Units | PV Ext Range Low | PV Ext Range High | PV Format | PV Char - Daca | P&ID | Notes | User ID | Update Date | QNP Name | QNP Signature | QNP Date
FTY_30017 | Flow Comp - NH3/Air to Mixer | Q_PTCMPF | PT Flow Compensation | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | FTY_30017_L.DACA.PV | TI_30013.DACA.PV | PI_30014.DACA.PV | EQNB | Square Root | 0 | 10 | 360 | 1119.5 | 0 | 7500 | kg/hr | -217.5 | 7717.5 | D0 | None | QN-VT-30-D-0010 | C&I Sheet: 1L & 26 | Arunkumar | 2021-10-29
FTY_30037 | Flow Comp - Primary Air ex 30K001 | Q_PTCMPF | PT Flow Compensation | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | FTY_30037_L.DACA.PV | TI_30032.DACA.PV | PI_30033.DACA.PV | EQNB | Square Root | 0 | 10 | 523 | 1040 | 0 | 120000 | kg/hr | -3480 | 123480 | D0 | None | QN-VT-30-D-0011 | C&I Sheet: 1L & 26 | Arunkumar | 2021-10-29
FTY_30080 | Flow Comp - Sec. Air to 30C001 | Q_PTCMPF | PT Flow Compensation | AREA30 | (HOLD) | CPM_MCC2_01 | MCC2 | FTY_30080_L.DACA.PV | TIC_30081.DACA.PV | 889.675 | EQNB | Square Root | 0 | 10 | 353 | 991 | 0 | 21000 | kg/hr | -609 | 21609 | D0 | None | QN-VT-30-D-0021 | C&I Sheet: 1N & 30 | Arunkumar | 2021-10-29